## Slide 1
Chart: 11kV Distribution Network Voltage Profile under No-Load Condition
| A | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
0% PV Penetration | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
20% PV Penetration | 1.0004 | 1.0006 | 1.0008 | 1.0009 | 1.001 | 1.0004 | 1.0005 | 1.0006 | 1.0007 | 1.0007 | 1.0007 | 1.0006 | 1.0006 | 1.0006 | 1.0004 | 1.0006 | 1.0011 | 1.0016 | 1.0017 | 1.0005 | 1.0005 | 1.001 | 1.0012 | 1.0015 | 1.0015 | 1.0016 | 1.0009 | 1.0009 | 1.001 | 1.0004 | 1.0006 | 1.0006 | 1.0004 | 1.0008 | 1.001 | 1.001 | 1.0006 | 1.0007
40% PV Penetration | 1.0007 | 1.0012 | 1.0015 | 1.0018 | 1.0019 | 1.0007 | 1.0009 | 1.0013 | 1.0013 | 1.0013 | 1.0015 | 1.0011 | 1.0012 | 1.0013 | 1.0009 | 1.0012 | 1.0023 | 1.0032 | 1.0033 | 1.0009 | 1.001 | 1.0019 | 1.0024 | 1.0029 | 1.0031 | 1.0031 | 1.0018 | 1.0019 | 1.002 | 1.0009 | 1.0011 | 1.0012 | 1.0008 | 1.0015 | 1.0019 | 1.002 | 1.0013 | 1.0013
60% PV Penetration | 1.001 | 1.0017 | 1.0023 | 1.0026 | 1.0028 | 1.001 | 1.0013 | 1.0019 | 1.0019 | 1.002 | 1.0021 | 1.0016 | 1.0018 | 1.0018 | 1.0012 | 1.0018 | 1.0033 | 1.0047 | 1.0049 | 1.0013 | 1.0015 | 1.0028 | 1.0036 | 1.0043 | 1.0045 | 1.0047 | 1.0026 | 1.0027 | 1.003 | 1.0012 | 1.0016 | 1.0017 | 1.0012 | 1.0023 | 1.0028 | 1.003 | 1.0019 | 1.0019
80% PV Penetration | 1.0012 | 1.0022 | 1.003 | 1.0035 | 1.0037 | 1.0013 | 1.0017 | 1.0024 | 1.0026 | 1.0026 | 1.0028 | 1.0021 | 1.0023 | 1.0024 | 1.0016 | 1.0024 | 1.0044 | 1.0063 | 1.0065 | 1.0017 | 1.002 | 1.0037 | 1.0047 | 1.0056 | 1.006 | 1.0062 | 1.0035 | 1.0036 | 1.0039 | 1.0016 | 1.0021 | 1.0022 | 1.0015 | 1.003 | 1.0037 | 1.0039 | 1.0024 | 1.0025
100% PV Penetration | 1.0015 | 1.0027 | 1.0037 | 1.0043 | 1.0046 | 1.0016 | 1.0021 | 1.003 | 1.0031 | 1.0032 | 1.0035 | 1.0026 | 1.0028 | 1.003 | 1.002 | 1.0029 | 1.0055 | 1.0078 | 1.0081 | 1.0021 | 1.0024 | 1.0046 | 1.0058 | 1.007 | 1.0075 | 1.0077 | 1.0043 | 1.0045 | 1.0048 | 1.002 | 1.0026 | 1.0027 | 1.0018 | 1.0036 | 1.0045 | 1.0048 | 1.003 | 1.003
Upper | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
Lower | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95

## Slide 2
Chart: 11kV Distribution Network Voltage Profile under Peak-Load Condition
| A | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
0% PV Penetration | 0.9724 | 0.96682 | 0.96264 | 0.95984 | 0.95845 | 0.97213 | 0.97119 | 0.96876 | 0.96793 | 0.96779 | 0.96685 | 0.96436 | 0.96319 | 0.96266 | 0.97117 | 0.96994 | 0.96744 | 0.96677 | 0.96677 | 0.97148 | 0.97139 | 0.96467 | 0.96154 | 0.95911 | 0.95811 | 0.95753 | 0.95804 | 0.95739 | 0.95576 | 0.97039 | 0.9692 | 0.96901 | 0.97212 | 0.96478 | 0.96169 | 0.96059 | 0.96915 | 0.96912
20% PV Penetration | 0.97298 | 0.96767 | 0.96369 | 0.96103 | 0.9597 | 0.97274 | 0.97189 | 0.96965 | 0.96885 | 0.96872 | 0.96785 | 0.96518 | 0.96405 | 0.96356 | 0.97185 | 0.97082 | 0.96885 | 0.96866 | 0.96873 | 0.97219 | 0.97216 | 0.96592 | 0.96306 | 0.96087 | 0.95997 | 0.95943 | 0.95923 | 0.95861 | 0.95706 | 0.97107 | 0.97001 | 0.96985 | 0.97276 | 0.96582 | 0.96292 | 0.96188 | 0.97005 | 0.97002
40% PV Penetration | 0.97354 | 0.9685 | 0.96471 | 0.96219 | 0.96092 | 0.97333 | 0.97256 | 0.97052 | 0.96976 | 0.96964 | 0.96882 | 0.96598 | 0.9649 | 0.96443 | 0.97251 | 0.97167 | 0.97024 | 0.97053 | 0.97066 | 0.97288 | 0.97292 | 0.96714 | 0.96454 | 0.9626 | 0.9618 | 0.96131 | 0.96039 | 0.95981 | 0.95834 | 0.97173 | 0.9708 | 0.97066 | 0.97339 | 0.96684 | 0.96412 | 0.96315 | 0.97092 | 0.97089
60% PV Penetration | 0.97408 | 0.9693 | 0.96571 | 0.96332 | 0.96212 | 0.97389 | 0.97322 | 0.97137 | 0.97063 | 0.97052 | 0.96977 | 0.96676 | 0.96571 | 0.96528 | 0.97314 | 0.9725 | 0.9716 | 0.97237 | 0.97256 | 0.97355 | 0.97365 | 0.96833 | 0.966 | 0.96431 | 0.9636 | 0.96315 | 0.96153 | 0.96098 | 0.9596 | 0.97236 | 0.97156 | 0.97145 | 0.97399 | 0.96783 | 0.9653 | 0.96439 | 0.97177 | 0.97174
80% PV Penetration | 0.9746 | 0.97008 | 0.96669 | 0.96443 | 0.9633 | 0.97444 | 0.97384 | 0.97219 | 0.97149 | 0.97139 | 0.9707 | 0.96752 | 0.96651 | 0.9661 | 0.97376 | 0.9733 | 0.97293 | 0.97418 | 0.97444 | 0.9742 | 0.97436 | 0.9695 | 0.96743 | 0.96598 | 0.96537 | 0.96497 | 0.96265 | 0.96213 | 0.96083 | 0.97298 | 0.97231 | 0.97222 | 0.97457 | 0.9688 | 0.96645 | 0.96561 | 0.97259 | 0.97257
100% PV Penetration | 0.97509 | 0.97084 | 0.96765 | 0.96552 | 0.96445 | 0.97496 | 0.97445 | 0.97299 | 0.97232 | 0.97223 | 0.9716 | 0.96825 | 0.96728 | 0.9669 | 0.97435 | 0.97408 | 0.97424 | 0.97596 | 0.97628 | 0.97482 | 0.97504 | 0.97065 | 0.96884 | 0.96763 | 0.96712 | 0.96676 | 0.96374 | 0.96325 | 0.96204 | 0.97357 | 0.97303 | 0.97296 | 0.97513 | 0.96975 | 0.96758 | 0.9668 | 0.9734 | 0.97338
Upper | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
Lower | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95

## Slide 3
PV Penetration Levels | Generation Output (kW) | Network Losses (kW)
0% | 0 | 182.5
20% | 50 | 159
40% | 100 | 138
60% | 150 | 119.5
80% | 200 | 103.5
100% | 250 | 90

## Slide 5: Sectionalized Distribution Network
Chart: 11kV Distribution Network Voltage Profile under No-Load Condition Sectionalized
| A | B | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
0% PV Penetration | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346 | 0.97346
20% PV Penetration | 0.97377 | 0.97382 | 0.97407 | 0.97427 | 0.9744 | 0.97446 | 0.97416 | 0.97422 | 0.97391 | 0.97411 | 0.97464 | 0.97512 | 0.97518 | 0.97446 | 0.97472 | 0.97496 | 0.97505 | 0.9751 | 0.97391 | 0.97404 | 0.97406 | 0.97426 | 0.97444 | 0.9745 | 0.97379 | 0.97388 | 0.97407 | 0.97411 | 0.974 | 0.97404 | 0.97407 | 0.9739 | 0.97396 | 0.97435 | 0.97438 | 0.97446 | 0.97383 | 0.97408 | 0.97408
40% PV Penetration | 0.97407 | 0.97415 | 0.97467 | 0.97505 | 0.97531 | 0.97544 | 0.97485 | 0.97497 | 0.97435 | 0.97473 | 0.97579 | 0.97675 | 0.97688 | 0.97544 | 0.97595 | 0.97643 | 0.97662 | 0.97671 | 0.97435 | 0.9746 | 0.97465 | 0.97504 | 0.9754 | 0.97553 | 0.97412 | 0.9743 | 0.97468 | 0.97475 | 0.97453 | 0.97461 | 0.97467 | 0.97433 | 0.97446 | 0.97523 | 0.97529 | 0.97545 | 0.9742 | 0.97469 | 0.97469
60% PV Penetration | 0.97436 | 0.97448 | 0.97525 | 0.97583 | 0.97621 | 0.9764 | 0.97552 | 0.9757 | 0.97477 | 0.97534 | 0.97693 | 0.97837 | 0.97856 | 0.9764 | 0.97717 | 0.97789 | 0.97818 | 0.9783 | 0.97477 | 0.97515 | 0.97522 | 0.97581 | 0.97635 | 0.97654 | 0.97444 | 0.9747 | 0.97528 | 0.97537 | 0.97506 | 0.97517 | 0.97526 | 0.97475 | 0.97494 | 0.97609 | 0.97619 | 0.97643 | 0.97455 | 0.97529 | 0.9753
80% PV Penetration | 0.97464 | 0.97479 | 0.97581 | 0.97658 | 0.97709 | 0.97735 | 0.97617 | 0.97641 | 0.97517 | 0.97594 | 0.97805 | 0.97997 | 0.98022 | 0.97734 | 0.97837 | 0.97932 | 0.97971 | 0.97987 | 0.97517 | 0.97569 | 0.97578 | 0.97656 | 0.97727 | 0.97753 | 0.97475 | 0.97509 | 0.97586 | 0.97599 | 0.97557 | 0.97572 | 0.97584 | 0.97516 | 0.97541 | 0.97695 | 0.97708 | 0.9774 | 0.9749 | 0.97588 | 0.97589
100% PV Penetration | 0.97492 | 0.97508 | 0.97636 | 0.97732 | 0.97796 | 0.97828 | 0.97681 | 0.97711 | 0.97556 | 0.97652 | 0.97915 | 0.98155 | 0.98187 | 0.97827 | 0.97955 | 0.98074 | 0.98122 | 0.98143 | 0.97556 | 0.9762 | 0.97632 | 0.97729 | 0.97819 | 0.97851 | 0.97504 | 0.97548 | 0.97644 | 0.9766 | 0.97607 | 0.97626 | 0.97641 | 0.97556 | 0.97588 | 0.9778 | 0.97796 | 0.97836 | 0.97524 | 0.97645 | 0.97647
Upper | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
Lower | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95

## Slide 6
Chart: 11kV Distribution Network Voltage Profile under Peak-Load Condition Sectionalized
| A | B | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
0% PV Penetration | 0.95444 | 0.94996 | 0.94422 | 0.9399 | 0.93702 | 0.93558 | 0.94521 | 0.94424 | 0.94869 | 0.94743 | 0.94486 | 0.94416 | 0.94416 | 0.94199 | 0.93878 | 0.93627 | 0.93523 | 0.93464 | 0.94789 | 0.94666 | 0.94647 | 0.94211 | 0.93893 | 0.93779 | 0.95417 | 0.95321 | 0.95072 | 0.94986 | 0.9462 | 0.94501 | 0.94446 | 0.95351 | 0.95341 | 0.93972 | 0.93905 | 0.93738 | 0.95416 | 0.95112 | 0.95108
20% PV Penetration | 0.95488 | 0.95049 | 0.94502 | 0.94092 | 0.93818 | 0.93681 | 0.94611 | 0.94521 | 0.94933 | 0.94826 | 0.94624 | 0.94605 | 0.94611 | 0.94321 | 0.94027 | 0.93802 | 0.93708 | 0.93653 | 0.94852 | 0.94743 | 0.94727 | 0.94312 | 0.94013 | 0.93906 | 0.95464 | 0.95376 | 0.95147 | 0.95065 | 0.94689 | 0.94573 | 0.94522 | 0.95408 | 0.95405 | 0.94078 | 0.94014 | 0.93856 | 0.95466 | 0.95188 | 0.95184
40% PV Penetration | 0.95531 | 0.95101 | 0.94582 | 0.94191 | 0.93931 | 0.93801 | 0.94699 | 0.94615 | 0.94995 | 0.94908 | 0.94761 | 0.94791 | 0.94804 | 0.94441 | 0.94174 | 0.93974 | 0.93891 | 0.93841 | 0.94914 | 0.94819 | 0.94804 | 0.94411 | 0.9413 | 0.9403 | 0.95509 | 0.95431 | 0.95221 | 0.95143 | 0.94756 | 0.94644 | 0.94596 | 0.95464 | 0.95467 | 0.94182 | 0.94122 | 0.93972 | 0.95516 | 0.95262 | 0.95259
60% PV Penetration | 0.95573 | 0.95151 | 0.94659 | 0.94289 | 0.94043 | 0.93919 | 0.94785 | 0.94707 | 0.95055 | 0.94988 | 0.94895 | 0.94975 | 0.94995 | 0.94559 | 0.94319 | 0.94144 | 0.94071 | 0.94025 | 0.94974 | 0.94892 | 0.9488 | 0.94508 | 0.94246 | 0.94153 | 0.95554 | 0.95484 | 0.95294 | 0.95219 | 0.94822 | 0.94714 | 0.9467 | 0.95518 | 0.95528 | 0.94285 | 0.94229 | 0.94087 | 0.95564 | 0.95335 | 0.95333
80% PV Penetration | 0.95613 | 0.952 | 0.94735 | 0.94386 | 0.94153 | 0.94036 | 0.9487 | 0.94799 | 0.95113 | 0.95067 | 0.95028 | 0.95157 | 0.95183 | 0.94675 | 0.94462 | 0.94313 | 0.9425 | 0.94208 | 0.95033 | 0.94964 | 0.94955 | 0.94603 | 0.94361 | 0.94274 | 0.95597 | 0.95536 | 0.95367 | 0.95295 | 0.94887 | 0.94784 | 0.94742 | 0.95572 | 0.95589 | 0.94388 | 0.94335 | 0.94201 | 0.95611 | 0.95408 | 0.95406
100% PV Penetration | 0.95653 | 0.95246 | 0.94809 | 0.9448 | 0.9426 | 0.94151 | 0.94952 | 0.94887 | 0.9517 | 0.95143 | 0.95159 | 0.95336 | 0.95369 | 0.94789 | 0.94603 | 0.94478 | 0.94426 | 0.94389 | 0.9509 | 0.95034 | 0.95027 | 0.94696 | 0.94473 | 0.94393 | 0.95639 | 0.95587 | 0.95437 | 0.95369 | 0.94951 | 0.94852 | 0.94813 | 0.95625 | 0.95648 | 0.94488 | 0.94439 | 0.94314 | 0.95657 | 0.95479 | 0.95477
Upper | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
Lower | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95

## Slide 7: Total Losses Sectionalized
PV Penetration Levels | Generation Output (kW) | Network Losses (kW)
0% | 0 | 190.5
20% | 50 | 165.9
40% | 100 | 144
60% | 150 | 124.7
80% | 200 | 108
100% | 250 | 93.9

## Slide 8
PV Generation Output (kW) | PV Penetration Level (%) | Three-Phase Fault Current at Peak Load Condition |  |  |  |  |  | Three-Phase fault Current at No-Load Condition |  |  |  |  | 
 |  | 33 kV Bus |  | 11 kV Busbar |  |  |  | 33 kV Bus |  | 11 kV Busbar |  |  | 
 |  | Current (A) | Increment (A) | Transformer A |  | Transformer B |  | Current (A) | Increment (A) | Transformer A |  | Transformer B | 
 |  |  |  | Current (A) | Increment (A) | Current (A) | Increment (A) |  |  | Current (A) | Increment (A) | Current (A) | Increment (A)
0 | 0 | 22500 | - | 16826 | - | 16849 | - | 22500 | - | 16907 |  | 16907 | -
50 | 20 | 22526 | 26 | 16845 | 19 | 16871 | 22 | 22524 | 24 | 16926 | 19 | 16930 | 23
100 | 40 | 22553 | 53 | 16865 | 39 | 16897 | 48 | 22550 | 50 | 16947 | 40 | 16956 | 49
150 | 60 | 22582 | 82 | 16886 | 60 | 16924 | 75 | 22577 | 77 | 16969 | 62 | 16985 | 78
200 | 80 | 22611 | 111 | 16909 | 83 | 16954 | 105 | 22605 | 105 | 16993 | 86 | 17015 | 108
250 | 100 | 22642 | 142 | 16933 | 107 | 16987 | 138 | 22634 | 134 | 17018 | 111 | 17049 | 142

## Slide 9: Contingency Condition
Chart: 11kV Distribution Network Voltage Profile under No-Load Contingency Condition
| A | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
0% PV Penetration | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347 | 0.97347
20% PV Penetration | 0.9739 | 0.97416 | 0.97435 | 0.97448 | 0.97455 | 0.97393 | 0.97401 | 0.97421 | 0.97424 | 0.97425 | 0.97431 | 0.97413 | 0.97417 | 0.9742 | 0.974 | 0.97419 | 0.97472 | 0.97521 | 0.97527 | 0.97403 | 0.9741 | 0.97455 | 0.9748 | 0.97504 | 0.97514 | 0.97518 | 0.97448 | 0.97451 | 0.97459 | 0.974 | 0.97413 | 0.97415 | 0.97397 | 0.97435 | 0.97453 | 0.97459 | 0.97421 | 0.97421
40% PV Penetration | 0.97428 | 0.97479 | 0.97518 | 0.97543 | 0.97556 | 0.97433 | 0.9745 | 0.97489 | 0.97495 | 0.97497 | 0.97509 | 0.97474 | 0.97482 | 0.97488 | 0.97447 | 0.97485 | 0.97591 | 0.97688 | 0.977 | 0.97453 | 0.97466 | 0.97556 | 0.97607 | 0.97655 | 0.97675 | 0.97683 | 0.97543 | 0.9755 | 0.97566 | 0.97447 | 0.97473 | 0.97477 | 0.9744 | 0.97516 | 0.97552 | 0.97565 | 0.97489 | 0.9749
60% PV Penetration | 0.97459 | 0.97536 | 0.97594 | 0.97633 | 0.97652 | 0.97467 | 0.97493 | 0.97551 | 0.97561 | 0.97563 | 0.97582 | 0.97529 | 0.9754 | 0.9755 | 0.97488 | 0.97546 | 0.97705 | 0.97849 | 0.97868 | 0.97498 | 0.97517 | 0.97651 | 0.97728 | 0.978 | 0.97829 | 0.97842 | 0.97633 | 0.97642 | 0.97666 | 0.97488 | 0.97527 | 0.97534 | 0.97479 | 0.97592 | 0.97646 | 0.97665 | 0.97552 | 0.97553
80% PV Penetration | 0.97486 | 0.97588 | 0.97665 | 0.97716 | 0.97742 | 0.97496 | 0.97531 | 0.97608 | 0.97621 | 0.97624 | 0.97648 | 0.97578 | 0.97594 | 0.97606 | 0.97524 | 0.97601 | 0.97812 | 0.98004 | 0.98029 | 0.97537 | 0.97563 | 0.97741 | 0.97844 | 0.97939 | 0.97978 | 0.97994 | 0.97716 | 0.97729 | 0.97761 | 0.97524 | 0.97576 | 0.97585 | 0.97511 | 0.97663 | 0.97734 | 0.9776 | 0.97609 | 0.9761
100% PV Penetration | 0.97506 | 0.97634 | 0.97731 | 0.97795 | 0.97827 | 0.97519 | 0.97563 | 0.97659 | 0.97675 | 0.97679 | 0.97709 | 0.97622 | 0.97641 | 0.97656 | 0.97554 | 0.9765 | 0.97914 | 0.98153 | 0.98185 | 0.97571 | 0.97603 | 0.97825 | 0.97953 | 0.98073 | 0.98121 | 0.98141 | 0.97794 | 0.9781 | 0.9785 | 0.97555 | 0.97619 | 0.97631 | 0.97539 | 0.97727 | 0.97817 | 0.97849 | 0.9766 | 0.97662
Upper | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
Lower | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95

## Slide 10
Chart: 11kV Distribution Network Voltage Profile under Peak-Load Contigency Condition
| A | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
0% PV Penetration | 0.92517 | 0.91941 | 0.9151 | 0.91223 | 0.9108 | 0.92489 | 0.9239 | 0.92135 | 0.92048 | 0.92034 | 0.91936 | 0.91683 | 0.91562 | 0.91507 | 0.92387 | 0.92259 | 0.91997 | 0.91927 | 0.91927 | 0.9242 | 0.9241 | 0.91721 | 0.91401 | 0.91152 | 0.91049 | 0.9099 | 0.91049 | 0.90983 | 0.90817 | 0.92305 | 0.9218 | 0.92161 | 0.92487 | 0.91729 | 0.9141 | 0.91297 | 0.92176 | 0.92172
20% PV Penetration | 0.92617 | 0.92068 | 0.91657 | 0.91383 | 0.91246 | 0.92592 | 0.92502 | 0.92268 | 0.92184 | 0.92171 | 0.92079 | 0.91807 | 0.9169 | 0.91638 | 0.92498 | 0.92389 | 0.92183 | 0.92164 | 0.92171 | 0.92534 | 0.92531 | 0.91889 | 0.91595 | 0.9137 | 0.91277 | 0.91223 | 0.91209 | 0.91146 | 0.90988 | 0.92415 | 0.92304 | 0.92287 | 0.92594 | 0.91876 | 0.91575 | 0.91468 | 0.92308 | 0.92305
40% PV Penetration | 0.92713 | 0.92189 | 0.91798 | 0.91538 | 0.91408 | 0.9269 | 0.9261 | 0.92395 | 0.92314 | 0.92302 | 0.92217 | 0.91926 | 0.91813 | 0.91764 | 0.92603 | 0.92515 | 0.92364 | 0.92395 | 0.92409 | 0.92643 | 0.92647 | 0.92051 | 0.91783 | 0.91584 | 0.91501 | 0.9145 | 0.91363 | 0.91304 | 0.91154 | 0.92521 | 0.92423 | 0.92408 | 0.92697 | 0.92017 | 0.91735 | 0.91634 | 0.92436 | 0.92433
60% PV Penetration | 0.92803 | 0.92307 | 0.91935 | 0.91688 | 0.91564 | 0.92784 | 0.92712 | 0.92517 | 0.9244 | 0.92429 | 0.9235 | 0.9204 | 0.91931 | 0.91885 | 0.92705 | 0.92636 | 0.92541 | 0.92623 | 0.92643 | 0.92748 | 0.92758 | 0.92207 | 0.91966 | 0.91792 | 0.91719 | 0.91673 | 0.91513 | 0.91457 | 0.91315 | 0.92622 | 0.92538 | 0.92526 | 0.92794 | 0.92153 | 0.9189 | 0.91796 | 0.92559 | 0.92557
80% PV Penetration | 0.9289 | 0.92419 | 0.92067 | 0.91833 | 0.91716 | 0.92873 | 0.9281 | 0.92636 | 0.92562 | 0.92551 | 0.92478 | 0.9215 | 0.92044 | 0.92002 | 0.92801 | 0.92753 | 0.92714 | 0.92846 | 0.92873 | 0.92847 | 0.92864 | 0.92359 | 0.92144 | 0.91995 | 0.91932 | 0.9189 | 0.91658 | 0.91605 | 0.91472 | 0.92719 | 0.92648 | 0.92638 | 0.92887 | 0.92285 | 0.9204 | 0.91952 | 0.92678 | 0.92676
100% PV Penetration | 0.9297 | 0.92526 | 0.92194 | 0.91973 | 0.91862 | 0.92956 | 0.92903 | 0.92749 | 0.92678 | 0.92669 | 0.92602 | 0.92254 | 0.92152 | 0.92113 | 0.92892 | 0.92864 | 0.9288 | 0.93062 | 0.93096 | 0.92942 | 0.92965 | 0.92506 | 0.92317 | 0.92192 | 0.92139 | 0.92101 | 0.91798 | 0.91747 | 0.91622 | 0.9281 | 0.92753 | 0.92746 | 0.92975 | 0.92411 | 0.92184 | 0.92103 | 0.92792 | 0.9279
Upper | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
Lower | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95

## Slide 11
PV Penetration Levels | Generation Output (kW) | Network Losses (kW)
0% | 0 | 229
20% | 50 | 199.7
40% | 100 | 173.5
60% | 150 | 150.3
80% | 200 | 130.1
100% | 250 | 112.9

## Slide 12
PV Generation Output (MW) | PV Penetration Level (%) | Three-Phase Fault Current at Peak Load Condition |  |  |  | Three-Phase fault Current at No-Load Condition |  |  | 
 |  | 33 kV Bus |  | 11 kV Busbar |  | 33 kV Bus |  | 11 kV Busbar | 
 |  | Current (A) | Increment (A) | Current (A) | Increment (A) | Current (A) | Increment (A) | Current (A) | Increment (A)
0 | 0 | 22500 | - | 12647 | - | 22500 | - | 12647 | -
50 | 20 | 22530 | 30 | 12673 | 26 | 22525 | 25 | 12673 | 26
100 | 40 | 22562 | 62 | 12707 | 60 | 22553 | 53 | 12706 | 59
150 | 60 | 22596 | 96 | 12747 | 100 | 22583 | 83 | 12746 | 99
200 | 80 | 22632 | 132 | 12794 | 147 | 22616 | 116 | 12793 | 146
250 | 100 | 22671 | 171 | 12847 | 200 | 22652 | 152 | 12847 | 200